Allocation of Responsibilities

Management

| Duty Holder – ________________________________ Type of Water System - | Client | C |
| --- | --- | --- |
|  | Anker Elemental | AE |
|  | Others / Subject to order | O |
| Service / Task | Frequency | Responsibility |
| Identification of the statutory Duty Holder, responsible person & deputies. |  |  |
| Notification to the local authority of any ‘Evaporative cooling devices’ |  |  |
| Conducting of a Legionellosis risk assessment |  |  |
| Provision of system schematics |  |  |
| Remedial or corrective actions required with priority / degree of risk |  |  |
| Programme for corrective action to be undertaken |  |  |
| Review of Legionellosis risk assessment |  |  |
| Production of the written scheme for prevention or control |  |  |
| Method Statements, COSHH, Risk assessments & Safety data sheets for works carried out. |  |  |
| Provision of control parameters, measurement methods, sample locations, and frequencies. |  |  |
| Emergency start-up and shut-down procedures |  |  |
| Description of normal and safe operation |  |  |
| Actions in the event of positive legionella results / outbreak |  |  |
| Providing training and identifying competence |  |  |
| Provision of a suitable record system (Logbook) |  |  |
| Maintaining the record system |  |  |
| Auditing the record system |  |  |
| The organisation responsible for completing a task is also responsible for supplying and maintaining records in the logbook for that tasks unless detailed below |  |  |

Allocation of Responsibilities

Evaporative Cooling System

| Task / Duty Required | Frequency | Responsibility |
| --- | --- | --- |
| Operational Conformance |  |  |
| Water Cleanliness |  |  |
| System Physical Condition |  |  |
| Analysis of Cooling Water: Conductivity, Oxidising Biocide, pH and Dipslides |  |  |
| Chemical Water Checks |  |  |
| Chemical Analysis of Cooling Water |  |  |
| Chemical Analysis of Make-up Water |  |  |
| Dipslide Tests |  |  |
| Conductivity Sensor Calibration |  |  |
| Uniformity of Water Distribution |  |  |
| Corrosion Rate Monitoring |  |  |
| Check of Chemical Reservoir |  |  |
| Condition of Sprays / Troughs |  |  |
| Condition of Eliminators |  |  |
| Condition of Pack |  |  |
| Condition of Pond |  |  |
| Condition of Immersion Heaters |  |  |
| Condition of Fan |  |  |
| Condition of Sound Attenuators |  |  |
| Legionella Sampling of Cooling Water |  |  |
| Cleaning and Chlorination |  |  |
| Review Meeting |  |  |
| Replenish Chemical Stocks |  |  |

Allocation of Responsibilities

Hot & Cold Water

| Type of Water System | Detail | Frequency | Responsibility |
| --- | --- | --- | --- |
| Calorifier inspection | Where an access hatch is fitted the internal condition should be evaluated and any debris removed. Where no hatch is fitted open the drain valve on the base of the vessel and comment on the temperature and visual condition of the water collected. (Drain cocks on the feed pipe or side of the vessel are not representative of the base of the vessel). | Annually |  |
| Water leaving and returning to the calorifier | Outgoing water should be at least 60 +/-2°C, and return at least 50°C (ideally closer to 55°C) If fitted, the thermometer pockets at the top of the calorifier and on the return leg are useful points for accurate temperature measurement. If installed, these measurements could be carried out and logged by a BMS system. | Monthly |  |
|  |  | Monthly |  |
| Sentinel Principal HWS return loop temperatures | This makes sure that the return temperatures on each principal loop are functioning as required. The water temperature should be at least 50°C when outlet water is not running. | Monthly |  |
|  |  | Monthly |  |
| Subordinate HWS return loops | Take the return temperatures on each subordinate loop (ideally monthly on a rota to cover all in a quarter). The water temperature should be at least 50°C when outlet water is not running. | Quarterly |  |
| Cold water services | Visually inspect cold water storage tanks and report remedial work where necessary. | Annually |  |
| Temperature profile | Take temperatures at a representative selection of other points to confirm they are below 20°C / above 50°C to create a temperature profile of the whole system over a defined time period. Peak temperatures or any temperatures that are slow to fall / rise should be an indicator of a localised problem. (minimum 25% of locations covered per annum). | Annually |  |
| Storage tank temperature monitoring | Check the tank water temperature remote from the ball valve and the incoming mains temperature. Record the maximum temperatures of the stored and supply water recorded by fixed maximum/minimum thermometers where fitted. | Annually |  |
| Type of Water System | Detail | Frequency | Responsibility |
| Sentinel cold tap temperatures | The water temperature should be below 20°C within 2 minutes of running the tap | Monthly |  |
|  |  | Monthly |  |
| Shower heads | Showerheads should be removed, disassembled, cleaned and disinfected. Or more frequently as required based on a risk assessment. In high-risk areas this should be done on a monthly basis. | Quarterly (monthly high risk areas) |  |
| Expansion vessel flushing | Where practical, flush through and purge to drain | Quarterly |  |
| TMV In Service Inspection | Fail safe and performance tests as required by TMV monitoring method statement and the recommendations of manufacturers. Pre-filters must be cleaned. | Annually |  |
| Flushing of little used outlets & deadlegs | Before carrying out flushing procedures, consideration should be given to removing infrequently used showers and taps. If they are removed, the redundant supply pipework should be cut back, as far as possible, to a common supply. | Weekly |  |
| OPTIONAL SERVICES (Not driven by L8) | TVC and Coliform sampling. |  |  |
|  | Legionella sampling. |  |  |

Allocation of Responsibilities

Other Systems

| Type of Water System | Service / Task | Frequency | Responsibility |
| --- | --- | --- | --- |
| Ultrasonic humidifiers/foggers and water misting systems. | If equipment fitted with UV lights, check to ensure effectiveness of lamp (check to see if within working life) and clean filters. | Six-monthly or according to manufacturer’s instructions |  |
|  | Ensure automatic purge of residual water is functioning | As part of machinery shut-down |  |
|  | Clean and disinfect all wetted parts | As indicated by risk assessment |  |
|  | Sampling for Legionella | As indicated by risk assessment |  |
| Spray humidifiers, air washer and wet scrubbers | Clean and disinfect spray humidifiers/air washers and make up tanks including all wetted surfaces, descaling as necessary | Six monthly |  |
|  | Confirm the operation of non-chemical water treatment if present | Weekly |  |
| Water softeners | Clean and disinfect resin and brine tank – check with manufacturers what chemicals can be used to disinfect the resin bed | As recommended by manufacturer |  |
| Emergency showers and eye-wash sprays | Flush through and purge to drain | Six monthly or more frequently if recommended by manufacturers |  |
| Sprinkler and hose reel systems | When witnessing tests of sprinkler blow-down and hose reels, ensure that there is minimum risk of exposure to aerosols. | As directed |  |
| Lathe and machine tool coolant systems | Clean and disinfect storage and distribution system | Six-monthly |  |
| Spa baths* *(modified routine) | Water treatment tests | Daily |  |
|  | Specialist monitoring, sampling & calibration | Monthly |  |
|  | Check filters – sand filters should be back-washed. | As directed |  |
| Horticultural misting systems | Clean and disinfect pipework distribution systems, spray heads and make up tanks including all wetted surfaces, descaling as necessary | Annually |  |
| Dental equipment | Drain down and clean | At the end of each working day |  |

| Type of Water System | Service / Task | Frequency | Responsibility |
| --- | --- | --- | --- |
| Car/bus washes | Check filtration and treatment systems, clean and disinfect systems | See manufacturer’s instructions |  |
| Indoor fountains and water features | Clean and disinfect ponds, spray heads and make up tanks including all wetted surfaces, descaling as necessary | Interval depending on condition |  |